Mount Duncan       21/12/2011
W.N. installed 40 Ah battery, disconnected all others.

Left the 70cm repeater disconnected, saving 250ma at night.
The battery box…………

Internal size,   900 by 920 by 470mm high.

Old 2 volt cells are Dunlop Type 2HR 539.

Each cell   is   290 by 185 by 460mm high.

Current drawn,  2m repeater alone  RX  250ma, TX  4.6A. (This is all that is operational now.)
With 70cm and link radio on, total RX current drawn is 500ma.

As I left, in cloudy conditions, the regulator was slowly cycling in ‘float’ mode, 13.0 to 13.3 volts.

70 cm repeater when on TX draws 7 amps.
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